## Slide 1
DPPA Case 3 Saigon18 Bridge Final Decision
April 2026
ALLOTROPE
Partner: Tara | USAID

## Slide 2
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation
2
Executive Summary
Project | Saigon18 DPPA Case 3
Decision | REJECT CURRENT CASE
Buyer Payment | 353.9B VND/yr (vs EVN 351.0B VND/yr)
Matched Renewable | 6.8 GWh/yr (3.7% of 184 GWh load)
Developer DSCR | -0.175 (required ≥ 1.0)
Developer NPV | -$6.05M USD (after-tax)

## Slide 3
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation
3
CONTEXT & APPROACH

## Slide 4
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation
4
Key Findings
Buyer Gate
FAIL — DPPA payment 353.9B VND/yr exceeds EVN benchmark 351.0B VND/yr by 2.9B VND/yr.
Developer Gate
FAIL — Min DSCR = -0.175, after-tax NPV = -$6.05M. Revenue covers only 59% of debt service.
Strike Anchor
5%-below-EVN (1,810 VND/kWh) is too low. ~3,900+ VND/kWh needed to clear developer DSCR ≥ 1.0.
BESS Impact
Minimal matched renewable — 6.8 GWh/yr covers only 3.7% of 184 GWh annual load. 96.3% served by EVN.
Recommendation
Reject current case. Reopen only with higher strike, smaller sizing, or actual 8760 load data.

## Slide 5
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation
5
ANALYSIS & RESULTS

## Slide 6
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation
6
Financial Summary
Metric | Value | Gate
Buyer Premium | +2.9B VND/yr | < 0 (vs EVN)
Matched Renewable | 6.8 GWh/yr | —
Developer DSCR | -0.175 | ≥ 1.0
Developer NPV | -$6.05M USD | > 0
Gate Comparison
Buyer Premium
Renewable %
DSCR
NPV

## Slide 7
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation
7
Physical Sizing & Methodology
• Bounded-optimization REopt solve with storage floor: PV=4800kW, BESS=1500kW/3300kWh.
• Synthetic DPPA settlement: min(load, generation) rule with strike + adder + KPP × CFMP.
• Buyer benchmark: EVN bill under same TOU tariff. Developer: PySAM Single Owner model.
• Controller gap analysis: fixed-window dispatch vs REopt free dispatch.
• Site-consistent data: saigon18 load + CFMP + FMP + TOU all from same workstream.

## Slide 8
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation
8
NEXT STEPS & DECISION

## Slide 9
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation
9
Next Steps
1. Reject current case under current strike and sizing assumptions.
2. Run strike sensitivity sweep (0%, 5%, 10%, 15%, 20% below EVN) to find viable band.
3. Remove storage floor and run free REopt optimization for optimal PV+BESS sizing.
4. Obtain actual monthly EVN bills and 8760 load profile for site validation.
5. Complete 22kV two-part tariff branch analysis and compare against TOU branch.

## Slide 10
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation
10
Thank You
Questions? contact@allotrope.vc
ALLOTROPE
Partner: Tara | USAID