## Slide 1
ALLOTROPE
Ninhsim DPPA Case 1
Private-Wire Solar Feasibility Screening
April 2026

## Slide 2
Executive Summary
Key findings at a glance
Project: Ninhsim DPPA Case 1 — Private-wire solar feasibility for the Ninhsim industrial facility.REopt PV Sizing: 38.11 MW — zero battery selected under the current case objective.Strike Basis: 1,012 VND/kWh (south-region Decree 57 ceiling).Finance: Project IRR 0.0% — does not clear the 15.0% hurdle.Recommendation: needs_reprice_or_resize — the case requires repricing or a bounded resize before advancing.
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation

## Slide 3
CONCLUSIONS & RECOMMENDATIONS
DPPA Case 1 — Initial Screening Results
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation

## Slide 4
Key Findings
Five critical observations from the Case 1 analysis
Substantial Solar Resource
REopt sized 38.11 MW PV, delivering 48.7 GWh annually with minimal curtailment (2.1 GWh) and zero grid export.
Zero Battery Adoption
REopt selected 0 MW / 0 MWh BESS under the private-wire objective. The 2-hour duration lock did not change the optimal result.
Below Hurdle Returns
Project IRR of 0.0% falls well short of the 15.0% target. Repricing or resizing is required before the case can advance.
Export-Free Design
The case enforces a no-export-intent design (0.0% export fraction), keeping the private-wire strike ceiling intact.
Sensitive to Assumptions
The combined decision is needs_reprice_or_resize, driven primarily by strike and capex sensitivity in the current basis.
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation

## Slide 5
Analysis Detail — Energy Results
REopt vs PySAM energy comparison
Metric | REopt | PySAM
PV Capacity (MW) | 38.11 | 38.11
BESS (MW / MWh) | 0.00 / 0.00 | 0.00 / 0.00
Annual Delivered (GWh) | 48.704 | 48.704
Export (GWh) | 0.000 | 0.000
Curtailment (GWh) | 2.055 | 2.055
Export Fraction (%) | 0.000 | 0.000
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation

## Slide 6
Financial Summary
Private-wire economics and IRR screening
Metric | Value | Target | Status
Strike (VND/kWh) | 1,012 | — | Ceiling basis
Project IRR (%) | 0.0% | 15.0% | Below hurdle
Equity IRR (%) | 0.0% | 15.0% | Below hurdle
Recommendation | needs_reprice_or_resize |  | Advance blocked
Recommendation: needs_reprice_or_resize
The current case does not clear the IRR hurdles. Repricing or a bounded resize is required before advancing.
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation

## Slide 7
Tools & Methodology
Stack used for Case 1 analysis
REopt.jl — First-pass PV+BESS sizing with Vietnam tariff defaults and Decree 57 ceiling.PySAM (PVWatts + Battwatts + Single Owner) — Fuller finance screen with private-wire strike and zero sell rate.Integration Bridge — Maps REopt sizes into PySAM and compares energy alignment.Decision Logic — Combined screening: negligible export + IRR hurdles must both clear.Limitations: PySAM uses PVWatts+Battwatts (not Pvsamv1). REopt is the first-pass sizing truth. Material REopt-PySAM mismatch triggers bounded iteration.
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation

## Slide 8
Next Steps & Open Questions
Seeds for the next analysis pass
Resize or Reprice — Decide whether the next pass should change strike, capex assumptions, or REopt size bounds.REopt-PySAM Loop — Add a bounded resize loop if REopt and PySAM disagree materially on export or curtailment.Interim Reports — Add automated phase-A/B/C HTML report generation if this becomes the preferred template.Current Status: needs_reprice_or_resize — do not advance without repricing or a bounded resize.
Confidential — For Internal Use by Allotrope & Key Partners — Not Approved for Further Circulation

## Slide 9
Thank You
Questions & Discussion
Tung Ho tah@allotropepartners.com Allotrope Partners — Vietnam Energy Storage